## Sheet1
SETRA PARTICLE COUNTER 5000 BACNET OBJECT LIST Rev. 1.2
BACnet Object List for ICC Gateway | Column1 | Column2 | Column3
Object Name | Object Type | Object Instance
Start Stop Sampling | AV | 1 | Write: 0 = Stop Sampling 1 = Start Sampling Read: Sampling State 0 = Stopped 1 = Delay 2 = Counting 3 = Hold
Device Status | AI | 1 | One bit for each status 0x0001 Flow Error 0x0002 Laser Error 0x0004 Time of day clock not running 0x0008 Internal Data Error Note: Flow Error and Laser Error will be true when not counting.
Cycle Count | AV | 2 | 0 = Continuous
Delay Time | AV | 3 | 0 - 359999 (99h, 59m, 59s)
Sample Time | AV | 4 | 0 - 359999 (99h, 59m, 59s)
Hold Time | AV | 5 | 0 - 359999 (99h, 59m, 59s)
Sample Mode | AV | 6 | 0 = Automatic 1 = Manual 2 = RT Meter
Mass Mode | BV | 1 | Enables PM
Use Recipes | BV | 2
Record Count | AI | 2
Sample Duration | AI | 3
Sample Flow Rate | AI | 4
Sample Status Bits | AI | 5 | Bit Mask (one bit for each status) 0x0001 -> Laser Ok 0x0002 -> Flow Ok 0x0004 -> Temperature Ok 0x0008 -> Relative Humidity Ok 0x0010 -> CO2 Ok 0x0020 -> TVOC Ok 0x0040 -> Barometric Pressure Ok 0x0080 -> Timestamp is invalid
Temperature | AI | 6 | If temperature = 999 No device If temperature = 998 Sensor Error Otherwise temperature at beginning of sample or if a temperature alarm occurred during the sample then the temperature when the alarm was detected.
RH | AI | 7 | If RH = 0 No device If RH = 1 Sensor Error Otherwise same logic as temperature
BP | AI | 8 | Absolute Barometric Pressure If BP = 0 Sensor Error
Alarm On | AI | 9 | 0 = Alarm on Differential Counts 1 = Alarm on Differential Counts / ft3 2 = Alarm on Differential Counts / m3 3 = Alarm on μg/m3 4 = Alarm on Sum Counts 5 = Alarm on Sum Counts / ft3 6 = Alarm on Sum Counts / m3 7 = Alarm on PM
Channel 1
Channel Enable | BV | 101
Alarm Enable | BV | 102
Alarm Threshold | AV | 101
Density Factor | AV | 102
Refractive Index | AV | 103
Alarm Flag | BI | 101
Channel Size | AI | 104 | μm
Differential Counts | AI | 105 | Count of Particles measured in this channel
Differential Counts per Cubic Foot | AI | 106 | Particles per cubic foot
Differential Counts per Cubic Meter | AI | 107 | Particles per cubic meter
Differential Mass | AI | 108 | Particle Mass in μg per cubic meter (μg/m3)
Sum Counts | AI | 109 | Sum of Particle counts in this and larger channels
Sum Counts per Cubic Foot | AI | 110 | Sum count per cubic foot
Sum Counts per Cubic Meter | AI | 111 | Sum count per cubic meter
Channel 2
Channel Enable | BV | 201
Alarm Enable | BV | 202
Alarm Threshold | AV | 201
Density Factor | AV | 202
Refractive Index | AV | 203
Alarm Flag | BI | 201
Channel Size | AI | 204 | μm
Differential Counts | AI | 205 | Count of Particles measured in this channel
Differential Counts per Cubic Foot | AI | 206 | Particles per cubic foot
Differential Counts per Cubic Meter | AI | 207 | Particles per cubic meter
Differential Mass | AI | 208 | Particle Mass in μg per cubic meter (μg/m3)
Sum Counts | AI | 209 | Sum of Particle counts in this and larger channels
Sum Counts per Cubic Foot | AI | 210 | Sum count per cubic foot
Sum Counts per Cubic Meter | AI | 211 | Sum count per cubic meter
PM | AI | 212 | Sum Particle Mass in smaller channels
Channel 3
Channel Enable | BV | 301
Alarm Enable | BV | 302
Alarm Threshold | AV | 301
Density Factor | AV | 302
Refractive Index | AV | 303
Alarm Flag | BI | 301
Channel Size | AI | 304 | μm
Differential Counts | AI | 305 | Count of Particles measured in this channel
Differential Counts per Cubic Foot | AI | 306 | Particles per cubic foot
Differential Counts per Cubic Meter | AI | 307 | Particles per cubic meter
Differential Mass | AI | 308 | Particle Mass in μg per cubic meter (μg/m3)
Sum Counts | AI | 309 | Sum of Particle counts in this and larger channels
Sum Counts per Cubic Foot | AI | 310 | Sum count per cubic foot
Sum Counts per Cubic Meter | AI | 311 | Sum count per cubic meter
PM | AI | 312 | Sum Particle Mass in smaller channels
Channel 4
Channel Enable | BV | 401
Alarm Enable | BV | 402
Alarm Threshold | AV | 401
Density Factor | AV | 402
Refractive Index | AV | 403
Alarm Flag | BI | 401
Channel Size | AI | 404 | μm
Differential Counts | AI | 405 | Count of Particles measured in this channel
Differential Counts per Cubic Foot | AI | 406 | Particles per cubic foot
Differential Counts per Cubic Meter | AI | 407 | Particles per cubic meter
Differential Mass | AI | 408 | Particle Mass in μg per cubic meter (μg/m3)
Sum Counts | AI | 409 | Sum of Particle counts in this and larger channels
Sum Counts per Cubic Foot | AI | 410 | Sum count per cubic foot
Sum Counts per Cubic Meter | AI | 411 | Sum count per cubic meter
PM | AI | 412 | Sum Particle Mass in smaller channels
Channel 5
Channel Enable | BV | 501
Alarm Enable | BV | 502
Alarm Threshold | AV | 501
Density Factor | AV | 502
Refractive Index | AV | 503
Alarm Flag | BI | 501
Channel Size | AI | 504 | μm
Differential Counts | AI | 505 | Count of Particles measured in this channel
Differential Counts per Cubic Foot | AI | 506 | Particles per cubic foot
Differential Counts per Cubic Meter | AI | 507 | Particles per cubic meter
Differential Mass | AI | 508 | Particle Mass in μg per cubic meter (μg/m3)
Sum Counts | AI | 509 | Sum of Particle counts in this and larger channels
Sum Counts per Cubic Foot | AI | 510 | Sum count per cubic foot
Sum Counts per Cubic Meter | AI | 511 | Sum count per cubic meter
PM | AI | 512 | Sum Particle Mass in smaller channels
Channel 6
Channel Enable | BV | 601
Alarm Enable | BV | 602
Alarm Threshold | AV | 601
Density Factor | AV | 602
Refractive Index | AV | 603
Alarm Flag | BI | 601
Channel Size | AI | 604 | μm
Differential Counts | AI | 605 | Count of Particles measured in this channel
Differential Counts per Cubic Foot | AI | 606 | Particles per cubic foot
Differential Counts per Cubic Meter | AI | 607 | Particles per cubic meter
Differential Mass | AI | 608 | Particle Mass in μg per cubic meter (μg/m3)
Sum Counts | AI | 609 | Sum of Particle counts in this and larger channels
Sum Counts per Cubic Foot | AI | 610 | Sum count per cubic foot
Sum Counts per Cubic Meter | AI | 611 | Sum count per cubic meter
PM | AI | 612 | Sum Particle Mass in smaller channels